ADEL ELECTRIC, LLC

ELECTRICAL PROPOSAL

Draft for internal review  ·  October 5, 2026  ·  Valid 30 days

# Project

| Project | Artemis Restaurant — tenant renovation, cellar and first floor |
| --- | --- |
| Address | 850 3rd Avenue, New York, NY 10022 |
| Prepared for | Kellari Hospitality · saa@kellarigroup.com |
| Prepared by | Adel Electric, LLC |
| Architect | Wid Chapman Architects · wid@widchapman.com |
| Engineer of record | ANZ Consulting Engineering, 259 West 30th Street, Suite 402, New York, NY 10001 |
| Drawings | Electrical E-001 through E-400 and Fire Alarm FA-001 through FA-200, Building Review, July 17, 2026 |
| Property | BIN 1036462 · Block 1306 · Lot 33 · Flood Zone X |
| Code basis | 2022 NYC Building Code, 2025 NYC Electrical Code, 2025 NYCECC; fire alarm per Appendix Q, NYC Fire Alarm rules, and NFPA 72 (2016) as amended |

# 1. Lump-sum base bid

Base Bid — Electrical and fire alarm for Artemis Restaurant: Five Hundred Forty-Eight Thousand and 00/100 Dollars ($548,000).

The base bid is the installed price for the scope in this proposal. It includes Division 26 power distribution from the existing 600 A tenant disconnect, branch power, mechanical and kitchen connections, lighting installation labor, emergency battery fixtures, Lutron pathway rough-in, a complete tenant fire alarm tied to the base-building fire command station, selective demolition, and Division 01 closeout. Lighting fixtures and Lutron Athena equipment are allowances, not part of the $548,000.

| Item | Description | Amount |
| --- | --- | --- |
| 01 | Division 01 — coordination, submittals, testing, as-builts, supervision | $32,000 |
| 26-A | Distribution: splice box, parallel 350 kcmil feeder (80 LF included), MDB, LP-C, LP-1, KP-C, KP-1, hood shunt-trip interfaces, grounding | $128,000 |
| 26-B | Branch power, devices, hood-equipment circuits, convenience and GFCI, security and AV empty raceway | $92,000 |
| 26-C | Mechanical power connections (water-source heat pumps, CWPs, MAU-1, OAF-1, TX-C-1, EJ-1) | $36,000 |
| 26-D | DWH-1 three-pole 200 A feeder and connection from MDB | $16,000 |
| 26-E | Lighting branch wiring and fixture hanging labor for 317 type-tagged fixtures. Fixtures are furnished by others. | $108,000 |
| 26-F | Emergency battery fixtures: 24 EM tags, Atlite-type, furnish and install | $16,000 |
| 26-G | Lutron pathway and rough-in: two Athena hub locations and 25 placeholder lighting circuits (15 cellar, 10 first floor) | $28,000 |
| 28 | Fire alarm: tenant FACP, devices on FA-100 / FA-101 / FA-200, Class B FPLP, base-building interface, programming, acceptance test | $74,000 |
| 26-H | Selective demolition and make-safe of existing tenant electrical in the area of work | $18,000 |
|  | Base bid | $548,000 |

# 2. Basis of proposal

This price is taken off the two landlord-review PDFs issued July 17, 2026:

EL set, 9 sheets: E-001, E-002, E-100, E-101, E-200, E-201, E-300, E-301, E-400. ANZ Consulting Engineering for Kellari Hospitality.

FA set, 4 sheets: FA-001, FA-100, FA-101, FA-200. Same engineer, client, and issuance.

Conduit on the plans is diagrammatic. Fixture type tags were counted once per occurrence on E-200 and E-201. Fire-alarm device counts are text labels on FA-100 and FA-101 inside the plan area. The architectural lighting fixture schedule, mechanical schedules, and a fully legible MDB panel schedule were not in this set. Those gaps are carried as qualifications, allowances, or RFIs.

# 3. Scope of work

## Division 01 — General requirements

Project electrical foreman, coordination with the GC, architect, ANZ, kitchen, hood, HVAC, and fire-alarm vendors, and building access rules.

Shop drawings and submittals for distribution equipment, disconnects, fire alarm, and the lighting-control rough-in.

NYC Bureau of Electrical Control filing labor and fire-alarm filing labor. Agency fees are reimbursable and are not in the base bid.

Testing, panel directories, as-builts, and O&M turnover.

## Division 26 — Electrical

Keep the existing 600 A disconnect that serves the tenant. Furnish a splice box above the ceiling in the engineer’s office and connect a new feeder to that existing feeder. Included feeder length is 80 linear feet of 2 sets of 4#350 kcmil copper in two 2-1/2 in. conduits. Additional length is a unit price.

New distribution: MDB, LP-C and LP-1 (each 400 A main-lug-only, 120/208 V, 3-phase 4-wire, 65 kA, 60-pole, 200% neutral, NEMA 1, surface), and kitchen panels KP-C and KP-1 (each 100 A main-lug-only, 120/208 V). Kitchen panels are fed through 3-pole 30 A shunt-trip breakers interlocked with the Type 1 hood Ansul systems.

LP-1 schedule demand, as printed: 72.25 kVA, 200.56 A at 208 V.

Branch circuits for receptacles, GFCI devices, equipment, and the noted NEMA 5-50R and NEMA 6-30R. Wire size increases from #12 to #10 on runs over 100 ft, with the shared-neutral rules on the plans.

Cellar equipment power: WSHP-C-1 through WSHP-C-5, CWP-1, CWP-2, TX-C-1, EJ-1, walk-in condensing units and evaporators, and DWH-1 at 3-pole 200 A from MDB.

First-floor equipment power: WSHP-1-1 through WSHP-1-5, MAU-1, and OAF-1. Kitchen equipment under the Type 1 hood is circuited to KP-1 or KP-C.

Hang and terminate 317 type-tagged lighting fixtures: cellar LT-1 (15), LT-2 (55), LT-7 (52), LT-9 (4); first floor LT-1 (33), LT-2 (36), LT-3 (38), LT-4 (22), LT-6 (12), LT-7 (40), R_DP01 (10). The fixture schedule is by the architect. Furnishing the fixtures is Allowance A1.

Furnish and install 24 emergency fixtures tagged EM (11 cellar, 13 first floor), integral 90-minute battery, wall-pack basis Atlite 6AC10-10-2-5.4-6RW5 where that catalog number is specified. EM fixtures are not on the Lutron system.

All normal lighting circuits are controlled by Lutron. Rough-in includes the cellar hub on the south wall of the mechanical room, the first-floor hub in the BOH utility hallway, and the engineer’s placeholder of 15 cellar and 10 first-floor 120 V lighting circuits. Athena equipment, modules, and factory startup are Allowance A2. E-301 is a concept sheet, not a construction drawing.

Empty conduit, drag line, boxes, and backboxes for the security system. Security devices are by others. Power to AV / IT head-end panels as shown. Low-voltage cable for AV, data, and music is by others, except fire alarm and the Lutron pathway.

Grounding, bonding, identification, and the seismic restraints specified for electrical equipment. The PE-stamped seismic calculations are by others.

## Division 28 — Fire alarm

New tenant fire-alarm control panel, 120 V from the line side of the tenant panel, Class B (NFPA Style 4 / Y / B), NYC-approved FPLP, 14 AWG notification, 16 AWG initiating.

Devices from the floor-plan labels, to be confirmed in the field before release:

Cellar: 14 smoke (F), 2 heat (H), 6 strobes (SL), 4 carbon-monoxide detectors with adjacent strobes, 5 monitor modules (MM1), 1 MM2, 2 duct detectors (SD), 3 relays (R), 3 weatherproof devices (WP), 1 tamper (TS), 1 waterflow (WF), 1 FACP.

First floor: 14 smoke (F), 3 heat (H), 1 strobe (SL), 7 carbon-monoxide detectors with adjacent strobes, 4 MM1, 1 MM2, 4 duct detectors (SD), 6 relays (R), 3 damper-related devices (D), 3 manual stations or holders (MH), 1 tamper, 1 waterflow, 1 remote annunciator (RA).

Alarm, trouble, and supervisory signals to the existing base-building fire command station in the main lobby. Two telco pairs to the voice/data demarc for central-station connection. Programming, acceptance test, and red junction-box identification. Monitoring contract and telco service are by the owner.

# 4. Scope matrix

| Item | Furnish | Install |
| --- | --- | --- |
| Distribution equipment, feeders, branch wiring, devices | Adel Electric | Adel Electric |
| Lighting fixtures (LT and R_DP types) | Others — Allowance A1 | Adel Electric |
| Emergency battery fixtures (EM tags) | Adel Electric | Adel Electric |
| Lutron Athena hubs, QSN modules, factory startup | Others — Allowance A2 | Adel Electric rough-in in base; equipment install with A2 |
| Shades and shade drives | Others | Others |
| Kitchen, hood, and Ansul equipment | Others | Others. Adel Electric provides power and shunt-trip / monitor wiring |
| HVAC and plumbing equipment, including DWH-1 | Others | Others. Adel Electric provides power connections |
| Fire-alarm panel and devices | Adel Electric | Adel Electric |
| Base-building fire command station | Existing | Interface only |
| Security devices and head-end | Others | Empty raceway by Adel Electric |
| AV / data cabling | Others | Others, except power and boxes shown |
| PE seismic calculations and sealed drawings | Others | Others |
| Cutting, patching, painting, ceiling replacement | GC | GC |

# 5. Unit prices

Unit prices apply to adds and deducts during construction. They assume normal hours, EMT, average runs as stated, and open-shop labor.

| Item | Unit | Price |
| --- | --- | --- |
| Additional 20 A branch circuit, average 75 ft homerun | each | $1,150 |
| Additional GFCI duplex, Decora, on an existing circuit | each | $285 |
| Owner-furnished lighting fixture, installed and circuited | each | $340 |
| 3/4 in. EMT with 2#12 and ground, installed | LF | $28 |
| 1 in. EMT, branch feeder, installed | LF | $36 |
| One set of 4#350 kcmil in 2-1/2 in. conduit, beyond the 80 LF included | LF | $185 |
| Core drill, 4 to 6 in., accessible slab or wall | each | $650 |
| Add or remove a 20 A breaker in an included panel | each | $185 |
| Fire-alarm smoke detector, installed and programmed | each | $485 |
| Fire-alarm strobe or horn/strobe, installed and programmed | each | $420 |
| After-hours journeyman, beyond the base schedule | hour | $248 |

# 6. Allowances and alternates

| No. | Type | Description | Amount |
| --- | --- | --- | --- |
| A1 | Allowance | Furnish lighting fixtures for the 317 type-tagged fixtures. Reconcile to the architectural fixture schedule and approved cuts. Installation labor stays in the base bid. | $165,000 |
| A2 | Allowance | Furnish Lutron Athena equipment for two QP5-1L-POE hubs, QSN modules for the 25 placeholder circuits, PoE switch, startup LTE modem, and factory startup. Shades are excluded. Reconcile to the final Lutron bill of materials. | $72,000 |
| ALT-1 | Alternate | After-hours or night work required by the building. Not in the base bid. Price from the unit rate once the hours are known. | Unit rate |
| ALT-2 | Alternate | IBEW or building-required union labor. The base bid is open shop. This alternate is quoted after the building labor rule is confirmed. | To be quoted |
| ALT-3 | Alternate | Adel Electric furnishes and installs exit signs where the plans require them and the symbol count is confirmed. Exit signs are specified; they are not separately type-tagged on these sheets. | To be quoted |

# 7. Qualifications and assumptions

The existing 600 A disconnect, and the service ahead of it, are adequate and remain. This proposal is not a service upgrade and not a Con Edison filing for new service.

The parallel 350 kcmil feeder included in the base bid is 80 linear feet, measured along the installed route. The drawings do not dimension that route.

MDB bus rating is assumed to match the 600 A source. The MDB schedule graphic on E-400 was not legible enough to copy circuit by circuit. Confirmation is RFI-1.

One type tag on E-200 or E-201 is one fixture. Shared circuit numbers next to fixtures were not counted as extra fixtures.

Normal weekday hours, freight-elevator access, and a staging area inside the tenant space are available. Work above 12 ft uses GC-provided lifts or scaffold.

Cutting, patching, painting, and ceiling replacement are by the GC. Adel Electric firestops its own penetrations.

Labor is open-shop NYC commercial labor. A union requirement is ALT-2.

These sheets are a landlord building-review issue, not a DOB-approved set. Changes after DOB or landlord comments are change orders.

Sales tax is excluded. A capital-improvement certificate (ST-124), if the owner provides one, will be used.

# 8. Exclusions

Furnishing architectural lighting fixtures, except under Allowance A1.

Lutron equipment purchase, shade equipment, and Lutron factory programming, except under Allowance A2.

Kitchen equipment, hoods, Ansul tanks and mechanical installation, HVAC equipment, and plumbing equipment.

Low-voltage cabling for data, voice, music, and security, and all security devices.

Central-station monitoring contract and telco service.

Replacement of the base-building fire command station.

Con Edison fees, landlord fees, DOB fees, FDNY fees, and BEC permit fees. Filing labor is included; fees are reimbursable at cost.

Temporary power and temporary lighting for other trades.

Abatement of hazardous materials.

PE structural calculations for seismic restraints, and any sealed engineering.

Patching, painting, flooring, and millwork.

Overtime, shift work, and union premium.

# 9. RFI log

| RFI | Question | Price effect |
| --- | --- | --- |
| 1 | Confirm MDB bus, main device, AIC, and feeder size from a legible panel schedule. | May change 26-A |
| 2 | Field-measure the route from the existing 600 A disconnect through the engineer’s office splice to the MDB. | Unit price beyond 80 LF |
| 3 | Issue the architectural lighting fixture schedule and confirm who buys the fixtures. | Allowance A1 |
| 4 | Issue final Lutron zoning, keypad, sensor, and shade counts. E-301 says quantities are TBD and the sheet is conceptual. | Allowance A2 |
| 5 | Provide available fault current at the existing 600 A disconnect. | AIC of gear |
| 6 | Confirm DWH-1 nameplate against the 3-pole 200 A circuit on E-100. | May change 26-D |
| 7 | Name the base-building fire-alarm manufacturer and the required interface at the lobby fire command station. | May change Division 28 |
| 8 | State whether 850 3rd Avenue requires union labor or after-hours work. | ALT-1 and ALT-2 |
| 9 | Confirm exit-sign quantity. The plans describe exit lights; they are not type-tagged the way LT fixtures are. | ALT-3 |

# 10. Commercial terms

Progress payments on AIA G702/G703, or the owner’s equivalent, against the schedule of values above.

Retainage 10% until substantial completion, then reduced as the contract states.

Payment is due 30 days after a certified application.

Changes in drawings, equipment, routing, access, or agency comments are change orders. Unit prices are the basis where they apply. Time and material uses the rates below, with 25% markup on materials.

T&M rates for this project: apprentice $95/hr, journeyman $165/hr, foreman $185/hr, master/project electrician $195/hr. After-hours is 1.5 times the applicable rate. These rates replace the Florida rate card for work on this New York job.

This proposal is valid for 30 days, through November 4, 2026.

Governing law and venue: State of New York, New York County.

Florida EC13016381 is Adel Electric’s Florida certified electrical contractor license. Work in New York City will be performed under a NYC-licensed master electrician, and BEC permits will be pulled in that license. The NYC license number will be added before this draft is issued for signature.

# 11. Acceptance

This draft is for Adel Electric’s review before it is sent. It is not an offer until it is signed and the NYC license block is completed.

Accepted by Kellari Hospitality:

Name / title: ________________________________    Date: ______________

Signature: ___________________________________

Base bid accepted: $548,000

Allowance A1 (fixtures):  ☐ accept $165,000    ☐ decline

Allowance A2 (Lutron equipment):  ☐ accept $72,000    ☐ decline